HALFEN USA Inc.		March 2012

8521 FM 1976

P.O. Box 547

Converse, TX 78109

Toll Free	800-423-9140

Fax	888-277-1695

Website	www.halfenusa.com

E-mail	info@halfenusa.com

Product Guide Specification

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The CSI Construction Specifications Practice Guide.

This section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” after editing this section.

Section numbers are from MasterFormat 2011 Update.

- 05 05 23

FRAMING AND MOUNTING CHANNELS

Specifier Notes:  This section covers Halfen framing and mounting systems “HM” site-installed, plain back or slotted channels, attached to structural substrate, for attaching equipment, piping, ductwork, and elevator guide rails.  Consult Halfen USA for assistance in editing this section for the specific application.

  - GENERAL

    - SECTION INCLUDES

Specifier Notes:  Edit the following for the specific application.

      - Steel channels [bolted]  [welded] to structural substrate.

    - RELATED REQUIREMENTS

Specifier Notes:  Edit the following list of related sections as necessary.  Limit the list to sections with specific information that the reader might expect to find in this section, but is specified elsewhere.

      - Section 05 12 00 – Structural Steel Framing:  [Bolting]  [Welding] to structural steel.

    - REFERENCE STANDARDS

Specifier Notes:  List standards referenced in this section, complete with designations and titles.  Delete standards not included in the edited section.  Including a standard in this list does not require compliance with that standard.

      - ASTM A123/A123M – Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products.

      - ASTM A283/A283M – Standard Specification for Low and Intermediate Tensile Strength Carbon Steel Plates.

      - ASTM A666 – Standard Specification for Annealed or Cold-Worked Austenitic Stainless Steel Sheet, Strip, Plate, and Flat Bar.

      - ASTM A1011/A1011M – Standard Specification for Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, and Ultra-High Strength.

      - ASTM B633 – Standard Specification for Electrodeposited Coatings of Zinc on Iron and Steel.

      - ASTM F568M – Standard Specification for Carbon and Alloy Steel Externally Threaded Metric Fasteners.

      - ASTM F738M – Standard Specification for Stainless Steel Metric Bolts, Screws, and Studs.

      - AWS B2.1/B2.1M – Specification for Welding Procedure and Performance Qualification.

      - AWS D1.1/D1.1M – Structural Welding Code – Steel.

    - COORDINATION

      - Coordinate the Work with installation and placement of the structural substrate.

      - Coordinate welding in accordance with AWS B2.1/B2.1M.

    - PREINSTALLATION MEETINGS

Specifier Notes:  Edit preinstallation meetings as necessary.  Delete if not required.

      - Convene preinstallation meeting [1 week]  [2 weeks] before start of work of this section.

      - Require attendance of parties directly affecting work of this section, including Contractor, Architect, Engineer, installer, and manufacturer’s representative.

      - Review materials, preparation, installation, tolerances, protection, and coordination with other work.

    - SUBMITTALS

Specifier Notes:  Edit submittal requirements as necessary.  Delete submittals not required.

      - Comply with Section 01 33 00 – Submittal Procedures.

      - Product Data:  Submit manufacturer’s product data, including installation instructions.

      - Shop Drawings:

        - Submit manufacturer’s shop drawings, indicating component profiles, sizes, connection attachments, size and type of fasteners, and accessories.

        - Indicate welded connections using standard welding symbols.

        - Indicate net weld lengths.

      - Manufacturer’s Certification:  Submit manufacturer’s certification that materials comply with specified requirements and are suitable for intended application.

      - Warranty Documentation:  Submit manufacturer’s standard warranty.

    - QUALITY ASSURANCE

      - Manufacturer’s Qualifications:

        - Capable of providing field service representation during installation.

        - Minimum of 10 years experience in manufacture of framing and mounting components.

        - Experience in projects of similar scope.

        - Manufacture in accordance with established quality assurance program.

    - DELIVERY, STORAGE, AND HANDLING

      - Delivery and Acceptance Requirements:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

      - Storage and Handling Requirements:

        - Store and handle materials in accordance with manufacturer’s instructions.

        - Keep materials in manufacturer’s original, unopened containers and packaging until installation.

        - Store materials in clean, dry area indoors.

        - Protect materials and finish during storage, handling, and installation to prevent damage.

  - PRODUCTS

    - MANUFACTURER

      - Halfen USA Inc., PO Box 18687, San Antonio, TX 78218.  Toll Free 800-423-9140.  Fax 888-277-1695.  www.halfenusa.com.  info@halfenusa.com.

    - DESIGN CRITERIA

Specifier Notes:  Restrict statements to describe the combined result of the components used to assemble the system.  If more than one type and weight of load is anticipated, create a schedule of loads, types of framing and mounting channels, and locations.

      - Channel Assembly:

        - Tension Load:  ______ lbs (______ kN).

        - Shear Load:  ______ lbs (______ kN).

        - Longitudinal Load:  ______ lbs (______ kN).

    - MATERIALS

Specifier Notes:  Edit the following two paragraphs for the specific application.

      - Steel Channels for Attachment to Structural Substrate:  “HM” framing and mounting channels.

        - Channel Type:  Halfen “HM” [20/12]  [28/15]  [38/17]  [49/30]  [40/22]  [50/30]  [52/34]  [55/42]  [72/48].

        - Channel Material:  [Carbon steel, ASTM A283]  [Carbon steel, ASTM A1011]  [Stainless steel, ASTM A666].

      - Bolts, Nuts, and Washers:

        - Bolt-Type Fasteners:  T-head, in contact with channel slot faces, [carbon steel, ASTM F568M]  [stainless steel, ASTM F738M].

        - Bolt Diameter:  [1/2]  [5/8]  [3/4]  [______] inch ([12]  [16]  [20]  [______] mm).

        - Bolt Length:  ______ inches (______ mm).

        - Finish for Carbon Steel T-bolts:  [Hot-dip galvanized, ASTM A123]  [Mill finish]  [Zinc electroplating, ASTM B633].

        - Nuts:  [Carbon steel]  [Stainless steel].

        - Washers:  [Carbon steel]  [Stainless steel].

    - FABRICATION

      - Shop assemble items in largest practical sections for delivery to site.

      - Mechanical Fastenings:  Bolts, nuts, and washers, consistent with design of components.

    - FINISHES

      - Unprotected Steel:  Clean surfaces of rust, scale, grease, and foreign matter before finishing or galvanizing.

      - Do not prime or galvanize surfaces in direct contact with concrete or where field welding is required.

      - Structural Components:  Hot-dip galvanize after fabrication, ASTM A123.

  - EXECUTION

    - EXAMINATION

      - Examine areas and supports to receive framing and mounting channels.

      - Verify dimensions, tolerances, and method of attachment with other work.

      - Notify Architect of conditions that would adversely affect installation.

      - Do not begin installation until unacceptable conditions are corrected.

    - PREPARATION

      - Supply items required to be attached to substrate to appropriate sections.

    - INSTALLATION

      - Install channels in accordance with manufacturer’s instructions at locations indicated on the Drawings.

      - Install items plumb and level, accurately fitted, free from distortion or defects.

      - Placement on Substrate:

        - Provide for temporary placement to maintain true alignment until completion of erection and installation of permanent attachment.

        - Weld channels to steel structural members in accordance with manufacturer’s instructions to achieve load transfer.

        - Field weld components indicated on shop drawings.

      - Obtain approval from Architect and manufacturer before site cutting or making adjustments not scheduled.

      - Perform field welding in accordance with AWS D1.1/D1.1M where necessary using certified welders.

    - TOLERANCES

Specifier Notes:  Edit the following sentence.

      - Channel Maximum Variation from [Plumb]  [Level]:  [1/8]  [1/4]  [______] inch ([3]  [6]  [______] mm).

    - PROTECTION

      - Protect installed channels from damage during construction.

END OF SECTION